## Sheet1
FORM SAS-42 | [7 empty] | Establish Encumbrance |  | Contract Number
Rev. 07-04 | [5 empty] | Date: | 2012-12-03 | Yes No |  | CT2-785-1200000009
| Commonwealth of Kentucky |  |  |  |  | Page | 1 | Change Order No: |  | 3
Finance and Administration Cabinet
| Department for Facilities and Support Services |  |  |  |  | Of | 1 | Control No:
CHANGE ORDER
| (Advice of Change) | [6 empty] | Multiple Cost Distribution Document Attached? |  | Yes No
FUND | DEPT | UNIT | ACTIVITY |  | SUB-ACTIVITY |  | ACCT. TEMPLATE | OBJECT CODE |  | AMOUNT
C5M7 | 440 | UNIT | MS03 |  | 00 |  | UC5M7 | E703
VENDOR | [6 empty] | Vendor Number |  |  | Vendor Suffix
VC0000085904
Codell Construction Company
| 4475 Rockwell Road | [5 empty] | Bid Invitation No.:
| Winchester, KY 40392 | [7 empty] | RFB-255-12
[7 empty] | Agency: |  | Morehead State University
[7 empty] | Project: |  | Renovate West Mignon Hall
Complete Mailing Address
County: | [6 empty] | Project No.: |  | 440-C5M7-MS03-00
Rowan
THIS DOCUMENT SHALL BECOME AN AMENDMENT TO THIS CONTRACT AND ALL PROVISIONS OF THIS CONTRACT WILL APPLY THERETO
Item No |  | Itemized Description of Change(s)* (Attach Additional Documentation if Necessary) | [7 empty] | Amount (+)(-) of Change
1 |  | PR-02: Door Frame Repair Revisons | [7 empty] | -5830.28
Reason: Improvement over plans and specifications and Found Condition; Several door frames were to be replaced completely, but tile to remain adjacent to the frames, and casework above the frames would be affected greatly if the frames were replaced completely, therefore the frames were revised to be repaired, rather than replaced completely.
2 |  | PR-04: Stair A Firewall Addition | [7 empty] | 888.38
Reason: Compliance with the building code; A new fresh air new duct needed to run through the existing rated stair from the Mechanical Room to the exterior wall, located below the existing concrete landing. A new 2-hour rated fire wall needed to be built below the landing to the floor, to separate the duct from the stair enclosure.
3 |  | PR-05: Tub / Shower Plumbing Cleanout and Valves Additions | [7 empty] | 6227.25
Reason: Improvement over plans and specifications: Recommendation by the engineers to add cleanouts and ball valves to control each tub/shower independently, and to provide maintenance of this drain line per Suite.
4 |  | PR-05: Adding Steel Columns at Parapet Walls (Add 2 days) | [7 empty] | 3465.45
Reason: Found Condition: Two existing concrete columns did not extend to the top of the parapet as anticipated. The structural engineer recommended that two additional steel columns be added to brace the existing parapet wall and new channels above.
COMPLETION OF THIS BLOCK NOT REQUIRED WHEN AMENDING A/E CONTRACT | [8 empty] | Net Increase: | 4750.8
To the best of my knowledge and belief, the cost or pricing data submitted is accurate, complete and current.
[5 empty] | Facilities and Support Services Auditor |  |  | Date
Signed: | [8 empty] | Net Decrease: | 0
| Contractor |  |  | Date | Availability of Funds |  |  | Date
Signed: |  |  |  |  | ** APPROVED **
4679000
| Architect/Engineer |  |  | Date
EOP Architects |  |  |  |  | Project Engineer - Division of Engineering and Contract Admin. |  |  | Date | Original Contract Price
250555
Architect/Engineer Firm Name
CONTRACT COMPLETION DATE IS ALTERED BY 2 CALENDAR DAYS |  |  |  |  | Director - Division of Engineering and Contract Admin. |  |  | Date | Previous Change Order (Net)
4934305.8
REVISED FINAL COMPLETION DATE: |  | 2013-06-01
[5 empty] | Authorized Agent |  |  | Date | Revised Contract Price
*Reason for change(s) must be printed or typed on this form, front or back. Do not state reason(s) as: (1) requested by owner, or (2) requested by using agency.
EXAMPLE